## Slide 1
Server / Power Rack Cold Plate Engineering Development
建立可量產、可驗證、可模組化的 Rack-level 散熱工程平台
Delta Electronics | TMSBU | 2026 年 5 月
可量產
Design for Manufacturing 從 Concept 到 NPI 標準化流程
可驗證
Thermal / Fluid / Mechanical / Reliability 四維測試矩陣
可模組化
Chip → Rack → CDU 層層解耦 支援多元應用場景
Cold Plate Engineering Platform — 2026 技術開發藍圖 | CONFIDENTIAL
CONFIDENTIAL

## Slide 2
ENGINEERING REQUIREMENTS
系統層級散熱需求與 Cold Plate 設計目標
Cold Plate 設計必須同時滿足熱性能、流體力學、機械可靠、與可維修性四維度目標
Category
Target Value
Test Method
Status
Heat Load
300–800W per GPU chip (TBD)
Calorimetry
In Progress
Flow Rate
5–20 LPM per cold plate
Flow meter
Confirmed
Pressure Drop
< 30 kPa @ 15 LPM (TBD)
Differential pressure gauge
In Progress
Thermal Resistance
< 0.05°C-in²/W (TBD)
JEDEC thermal test
Not defined
Leak Rate
Zero leak — 100% helium test
Helium leak detector
Confirmed
MTBF
> 40,000h (CDU side)
Field / accelerated life test
TBD
Operating Temp
-40°C to +85°C (TBD)
Thermal cycling
TBD
Serviceability
Repair time < 30 min (target)
Time study
TBD
(TBD) = To Be Defined — 需要與 RD / PM / CSP 確認後更新 | Status colors: Green=Confirmed / Orange=In Progress / Red=Not defined
熱、流體、機械、可靠四維度目標必須同步追蹤，缺一不可

## Slide 3
APPLICATION LAYERS
從 Chip-level 到 Rack-level 的四層熱源架構
不同熱源有不同散熱介面與設計約束，需針對每層建立對應的 Cold Plate 解決方案
L1
Chip-level — GPU / ASIC
熱通量 > 500W/cm²，局部熱點明顯。介面：TIM → Cold plate base，Ra < 0.8μm，接觸壓力均勻分布。
→
L2
Power Module — IGBT / SiC
熱通量 200–400W/cm²，面積 50×50mm–100×100mm。介面：TIM 或焊接，雙面散熱可選。需電氣絕緣 > 3kV/mm。
→
L3
Power Rack — 48V Busbar / 400V Dist.
熱密度中等，散熱區域均勻。介面：整合至 busbar 結構，鋁合金擠型散熱片。與電源系統整合優先。
→
L4
Rack-level — Manifold / Cooling Plate
分配冷卻介質至多個 Cold Plate。介面：Quick disconnect / Manifold。流量平衡、壓力損失一致性設計重點。
每層熱源有不同的設計約束與驗證方法，需建立對應的 Cold Plate 產品線，而非以單一設計覆蓋全部
四層熱源分類是 Cold Plate 產品線架構的基礎

## Slide 4
THERMAL ARCHITECTURE
熱傳路徑從晶片到設施的完整架構
Cold Plate 是熱從晶片到設施冷卻回路的關鍵節點，每一層都有其工程意義
Heat Source
GPU / ASIC / Power Module Heat generation point
→
TIM
Thermal Interface Material Fills micro-gaps
→
Cold Plate Base
Copper / Aluminum base Uniform heat spread
→
Channel / Fin
Fin + channel geometry Convective heat transfer
→
Coolant Flow
Water / glycol coolant Absorbs heat
→
CDU / Facility
Heat rejection to building Closed loop control
Heat flow
Coolant flow
Key Design Parameters
• Fin height / pitch / width
• Hydraulic diameter
• Surface roughness Ra
• Contact pressure distribution
• TIM selection & thickness
• Inlet / outlet ΔT < 10°C
Cold Plate 是熱傳路徑的瓶頸節點，需從系統層面優化

## Slide 5
CHANNEL DESIGN
五種主流流道設計方案的技術比較
不同流道幾何適用於不同熱密度與流量條件，需依應用場景選擇
Design
Advantage
Heat Flux Range
Complexity
Recommendation
Parallel Channel
Low δP, uniform flow, easy to manufacture
Medium heat flux < 300W/cm²
Low
Recommended (Power rack 48V)
Serpentine
Long path, good for high flux, slight δP penalty
Medium-high 300–450W/cm²
Medium
Applicable (GPU cold plate)
Pin Fin / Skived Fin
High area density, efficient heat transfer
High heat flux > 400W/cm²
High
Applicable (GPU cold plate)
Microchannel
Ultra-high HTC, minimal thermal resistance
Very high flux (limited by clogs)
Very High
Research only (Mass production TBD)
Hybrid Channel
Combines geometries, optimized for AI server
High density 200–500W/cm²
Medium-High
Preferred (Primary target)
Geometric diagrams (representative only — detailed CAD geometries to be defined in Phase 1)
流道幾何沒有最佳解，只有最適解 — 需依熱密度、壓降、量產三維度評估

## Slide 6
KEY PARAMETERS
Cold Plate 設計四類關鍵參數
設計驗證需從 Thermal / Fluid / Mechanical / Reliability 四個維度同步展開
Thermal
R_th (熱阻)
< 0.05°C-in²/W
TBD
Chip ΔT
< 5°C across chip
TBD
ΔT (inlet/outlet)
< 10°C at design flow
Confirmed
Contact pressure
0.5–2 MPa uniform
TBD
Fluid
Flow rate
5–20 LPM per cold plate
Confirmed
Pressure drop
< 30 kPa @ 15 LPM
In Progress
Flow uniformity
< 10% deviation per channel
TBD
Reynolds number
Re < 2300 (laminar) or Re > 4000 (turb)
TBD
Mechanical
Flatness
< 0.05mm
Confirmed
Thickness
< 6mm for GPU cold plate
TBD
Material strength
Al 6061-T6 yield > 270 MPa
Confirmed
Mount interface
Compatible with rack holder
TBD
Reliability
Thermal cycling
5,000 cycles -40°C/+85°C
TBD
Pressure test
1.5× max operating pressure
TBD
Vibration
Per rack environment (TBD)
TBD
Corrosion
Per water quality spec (TBD)
TBD
四類參數同步追蹤，是 Cold Plate 從設計到量產的品質把關核心

## Slide 7
MATERIALS & PROCESS
材料與製程評估 — 散熱性能 vs. 成本 vs. 可量產性
材料與製程的選擇決定了 Cold Plate 的散熱性能上限與量產成本，需在設計階段早期確認
Material
Thermal Conductivity
Cost
Mass Production
Application
Copper (Cu)
~400 W/m·K
High
CNC / Brazing
High-power GPU cold plate
Aluminum (6061/6063)
~150–180 W/m·K
Medium
FSW / Stamping / CNC
Medium-power / Power rack
Stainless Steel (SS)
~15 W/m·K
Medium
Stamping / Welding
Corrosion-sensitive applications
Hybrid (Cu base + Al fin)
~250–300 W/m·K effective
Medium-High
Brazing / FSW
Primary choice — high power AI server
Manufacturing Process Comparison
CNC Machining
Prototype / low volume
Brazing (釺焊)
High-power cold plate (primary)
FSW (攪拌摩擦焊)
High-volume Al production
Skiving
Pin fin cold plate (high performance)
Stamping
Power rack cold plate (simple geometry)
Surface Treatment
Corrosion protection + appearance
材料 + 製程聯合選擇決定性能上限與量產成本，需在 Concept 階段早期確認

## Slide 8
SEALING & LEAK MANAGEMENT
密封設計與漏液風險管理
漏液是液冷系統的頭號風險，密封設計必須從架構層面而非零件層面來處理
Seal Type
Cost
Leak Risk
Temp Range
Serviceability
O-ring
Low
Low (periodic replacement)
-40°C to +120°C
Easy — replaceable
Gasket
Medium
Medium (bolt torque critical)
-40°C to +150°C
Moderate
Welding / Brazing
High
Near-zero (permanent)
Wide range
Not serviceable
Compression Fitting
Medium
Low (if assembled correctly)
-40°C to +200°C
Moderate — disassemblable
Leak Risk Locations & Mitigation
• Cold plate body seam: Braze/weld → 100% He test
• Quick disconnect interface: O-ring + bubble sensor
• Manifold joints: Gasket + leak detection
• CDU connection: Compression fitting + pressure monitor
Serviceability target: Repair time < 30 min | Quick disconnect with hot-swap capability required
漏液風險需從架構層面管理，而非只靠單一密封技術

## Slide 9
VALIDATION WORKFLOW
從 Requirement 到 DFM 的標準工程驗證流程
Cold Plate 開發需要一個標準化的驗證流程，確保 design decision 有據可查、有數字支撐
S1
Requirement Mapping
System heat demand → Cold Plate specs Design Input Matrix
→
S2
Thermal Modeling
3D CAD + FEA thermal analysis Chip heat flux distribution
→
S3
CFD / Flow Simulation
Pressure drop, flow uniformity Sensitivity analysis
→
S4
Prototype Build
CNC / 3D print rapid prototype Brazing for production-representative
→
S5
Physical Testing
Thermal / fluid / mechanical / reliability Full validation test matrix
→
S6
DFM + NPI
Manufacturing feasibility review CPK / QC standard / CSP FAT
↩
Iteration loop: Failed tests return to Step 2 (Thermal/Fluid redesign) — target max 3 iterations per design cycle
Decision Gates: S1→S2 (Design Review) | S3→S4 (Prototype Go/No-Go) | S5→S6 (DFM Sign-off) | S6→Production (NPI Release)
標準化驗證流程是 Cold Plate Engineering Platform 的核心模組

## Slide 10
VALIDATION TEST MATRIX
Cold Plate 驗證測試矩陣 — Thermal / Fluid / Mechanical / System
四類測試構成完整的驗證框架，缺任何一類都無法確保產品達到量產品質
Thermal
R_th vs. flow rate
→ Pass: within 15% of simulation
Surface ΔT (IR imaging)
→ Pass: ΔT < 5°C
Inlet/outlet ΔT
→ Pass: ΔT < 10°C @ design flow
72h steady-state test
→ Pass: stable operation, no degradation
Fluid
P-Q curve (pressure vs. flow)
→ Pass: < 30kPa @ 15LPM
Flow uniformity (array)
→ Pass: deviation < 10%
Re number assessment
→ Confirm design assumption
Water quality corrosion test
→ Pass: no corrosion after 1,000h
Mechanical / Reliability
Pressure hold test
→ Pass: no leak at 30 min
Burst / hydrostatic test
→ Pass: > 3× rated pressure
Thermal cycling
→ Pass: no cracks, leak rate < 1×10⁻⁸ Pa·m³/s
Vibration test
→ Pass: no mechanical degradation
System-Level
CDU integration test
→ Pass: stable feedback control
QD hot-plug test
→ Pass: 100 cycles, no leak
Rack-level leak test
→ Pass: zero leak under working pressure
CSP FAT (customer)
→ Per customer spec (TBD)
四類測試缺一不可，測試矩陣需與客戶規格和系統需求同步更新

## Slide 11
RISK MANAGEMENT
六大技術風險與對應策略
風險需在設計階段早期識別，否則進入 NPI 後的補救成本將呈指數增加
R1
Pressure Drop Exceeds Target
L:H
I:H
→ CFD override → channel geometry optimization → set δP limit in design rule
Consequence: CDU pump overload, flow starvation, overheating
R2
Thermal Target Unmet
L:M
I:H
→ Build simulation→prototype→test fast iteration capability; TAT < 4 weeks
Consequence: Chip throttling, customer complaint, program delay
R3
Leakage Risk
L:L
I:H
→ Seal design review, 100% He test in production, leak sensor standard
Consequence: Data center incident, liability, brand damage
R4
Corrosion / Water Quality
L:M
I:M
→ Establish water quality spec; material selection (Ni-plated Cu) upfront
Consequence: Channel clogging, efficiency decline, high warranty cost
R5
Manufacturing Yield Risk
L:M
I:M
→ DFM review early in design; early supplier engagement
Consequence: Higher unit cost, NPI delay, supply shortage
R6
Field Service Difficulty
L:L
I:M
→ Modular design, QD standard, service manual, spare parts policy
Consequence: Longer downtime, high post-sale cost, low satisfaction
L = Likelihood | I = Impact | H=High / M=Medium / L=Low | RAG: Red=High risk / Orange=Medium
風險管理是持續性活動，需要跨團隊 Visibility，Engineering Platform 提供這個框架

## Slide 12
DEVELOPMENT ROADMAP
12 個月開發計畫 Roadmap — 從 Concept 到 NPI
三階段里程碑，確保每一階段都有可驗證的交付物，逐步建立 Cold Plate Engineering Platform
Phase 1 Concept
Month 0–2
• 建立工程需求矩陣（熱/流體/機械/可靠度）
• 完成流道設計方案篩選
• 材料與製程初步評估（CNC 打樣驗證）
• 建構 Thermal/Fluid 模擬能力（CAE 工具）
交付物：Engineering Requirements Spec + Concept Design Report
→
Phase 2 Prototype & Validation
Month 3–6
• 完成 Hybrid channel cold plate 詳細設計
• CNC prototype build（2–3 輪迭代）
• 執行完整驗證測試矩陣
• 建立 DFM checklist 與製造可行性審查
• CSP 客戶技術研討（確認介面相容性）
交付物：Prototype Report + Validation Test Report + DFM Review
→
Phase 3 NPI / Pilot Build
Month 7–12
• DFM 轉量產設計凍結
• 移轉至製造（與供應商建立生產流程）
• Pilot build（5–20 套，依客戶需求）
• Pilot 部署與現場驗證
• CSP 工廠驗收測試（FAT）
交付物：NPI Release + Pilot Build Report + CSP FAT Report
Resources required: Thermal/Fluid simulation tools (CAE), CNC prototype capability, Test equipment (TBD in Phase 1)
12 個月三階段，建立 Cold Plate Engineering Platform，目標 2027 上半年具備量產能力